#### Fire Safety Plan

(Restaurant)

Fire Safety Plan – Restaurant (Group A, Division 2) for:

(Business Name)

(Business Address)

Prepared By                                        Reviewed By

(Person Completing Form)                                            (Fire Inspector)

Signature						        Signature

Date of Approval

Table of Contents

Part #         Topic – PG #

# Part 1		Introduction:  PG 3

Part 2 (a)	Audit of Building Resources:  PG 4

Part 2 (b)	Audit of Human Resources:  PG 7

Part 3		Emergency Procedures for Occupants:  PG 8

Part 4		Emergency Procedures for Supervisory Staff:  PG 9

Part 5		Responsibilities of the Owner/Occupant:  PG 13

Part 6 	Fire Hazards — Commercial:  PG 14

Part 7		Fire Extinguishment, Control or Confinement:  PG 15

Part 8		Alternative Measures for Occupant Fire Safety:  PG 16

Part 9		Fire Drills:  PG 17

Part 10	Requirements of the Ontario Fire Code:	PG 18

Part 11	Maintenance Requirements of Building Fire

And Life Safety Systems:  PG 19

Part 12	Building Schematics, Site Plan/Floor Plan:  PG 30

Fire Department Contact Info:		PG 33

Part 1

Introduction

The Ontario Fire Code, Section 2.8 of Division B, requires the implementation of a FIRE SAFETY PLAN for this building/occupancy.  The plan is to be kept in the building in an approved location.

The implementation of the Fire Safety Plan helps to ensure effective utilization of life safety features in a building to protect people from fire.  The required Fire Safety Plan should be designed to suit the resources of each individual building or complex of    buildings.  It is the responsibility of the owner to ensure that the information contained within the Fire Safety Plan is accurate and complete.

The Fire Protection and Prevention Act Part VII, Section 28, states that in the case of an offence for contravention of the fire code, a corporation is liable to a fine of not more than $100,000 and an individual is liable to a fine of not more than $50,000 or imprisonment for a term of not more than one year or both.

This official document is to be kept readily available at all times for use by staff and fire officials in the event of an emergency.

The fire safety plan approved location is      .

SUBMISSION PROCEDURES

At least two (2) copies of the Plan (8 ½ X 11 format) must be submitted to the Chief Fire Official.  Upon approval, one copy will be returned to the author and one copy will be retained by the Fire Department.

The Chief Fire Official is to be notified regarding any subsequent changes in the         approved Fire Safety Plan.

Part 2(a)

Audit of Building Resources Checklist

Occupancy Type

Occupant Load: (if applicable)

Construction Type

Access

Designated Fire Route:		 No     Yes

Nearest Municipal

Hydrant Location:

| Private Hydrants: No Yes (Location(s)): |  |
| --- | --- |
| Lockbox: No Yes (Location(s)): |  |

Heating	 Propane	  Electric		 Other

| Main Gas Shut-off: No Yes (Location(s)): |  |
| --- | --- |

Main Electrical Shut-off Location:

Main Domestic Water Shut-off Location:

Fire Alarm System:	Make:

Model:

Main Panel Location:

Annunciator Panel Location:

Fire Alarm Description:

Sprinkler System:	   No      Yes 		Type:	 Wet    Dry   Other

Connected to the Fire Alarm System:  No      Yes

Location of Sprinkler Room/Shut Off Valves:

Fire Department

Connection:	No     Yes (Location(s)):

Fixed Extinguishing System for Commercial Cooking Equipment

No      Yes 		Type:

(i.e. Wet Chemical, Dry Chemical, CO2)

Connected to F/A System:     No      Yes

Ecology Unit:     No      Yes    	Protected by Fixed System:     No      Yes

Fuel Source:	 Natural Gas	 Electric		 Other

Fuel Shut Off for Appliances:	Location:

40BC Extinguisher:	Location:

K Type (wet) Extinguisher (if applicable):	Location:

Other Extinguishing Systems:

No      Yes – If YES, please list “Type” and “Area/Location Protected” in Part 2(a) Additional Information and label “Other Extinguishing Systems.”

Portable Fire Extinguishers (Location(s): Refer to Floor Plan)

No      Yes 		Type(s):

Extra Hazardous Area:  Description/Location: Eg: Confined Crawlspace / Under main building

Is there hazardous materials on site?		 No      Yes

If YES, please list the material and quantity in Part 2(a) Additional Information and label “Hazardous Materials”

Emergency Lighting

No      Yes 			Location(s):

Alternate Emergency Exits:	 No      Yes - Refer to schematics for location of exits.

Part 2(a)

Additional Information

Please print multiple copies of page if required.

For any additional information not already covered (Hazardous Materials, Back-up Power Systems, etc.):

Part 2(b)

Audit of Human Resources

Business/Building Name:

Address:		      Unit No.

Postal Code:	      Business Phone No.

Business Owner:

Address:

Postal Code:

Phone Number(s):

After Hour Contacts (24 hour telephone numbers)

Manager/Supervisor:       Phone No.

Employee/Title:	      Phone No.

Employee/Title:	      Phone No.

Other:		      Phone No.

Building Owner:

Address:

Postal Code:	       Phone No.

Fire Alarm Monitoring Company:       Phone No.:

Sprinkler Monitoring Company:       Phone No.:

Part 3

Emergency Procedures for Occupants

Please take the time to review this section (1 page).

Emergency procedures signage will be affixed to the wall at all fire alarm pull stations.

IN CASE OF FIRE

Upon Discovery of Fire:

- Leave fire area immediately and close doors

- Sound Fire Alarm

- Call 9-1-1 and ask for Fire

- Leave building via nearest Exit

- Do not use elevator

Upon Hearing Fire Alarm:

- Leave building via nearest Exit

- Close doors behind you

- Do not use elevator

- Wait in a safe location for the Fire Department.

CAUTION

IF YOU ENCOUNTER SMOKE - USE AN ALTERNATE EXIT

DO NOT re-enter the building until you are notified by the Fire Department that it is safe to do so.

Remain Calm

Part 4

Emergency Procedures for Supervisory Staff

Please take the time to review this section (2 pages).

Upon Discovery of Fire

- Leave fire area immediately and close doors.  Alert occupants.

- Sound Fire Alarm and follow the fire alarm supervisory procedures.

- Call 9-1-1 from a safe location.

- Use portable fire extinguisher ONLY IF the fire is small, your exit path is unobstructed and you are trained to do so.

- Exit the building via the nearest exit.

- Await the arrival of Fire Department at the main entrance.

Upon Hearing of a Fire Condition

- Turn off all cooking appliances.

- Ensure that the other occupants have been notified of the emergency conditions.

- Notify Bancroft Fire Department of the emergency condition. Dial 9-1-1 and ask for the Bancroft Fire Department.

- If it is safe to do so, supervise the evacuation of all occupants, including those       requiring assistance.

- Upon the arrival of the firefighters, inform the fire officer of the conditions in the building and co-ordinate the efforts of the Supervisory staff with those of the Fire Department.

- Provide access and vital information to the firefighters as to location of persons, master keys for this occupancy and service rooms, etc.

Related Duties

In general:

- Keep the doors in fire separations closed at all times unless the door is designed to automatically close in the event of a fire emergency.

- Keep access to exits and EXITS, inside and outside, clear of any obstructions at all times.

- Do not permit combustible materials to accumulate in quantities or locations that would constitute a fire hazard.

- Promptly remove all combustible waste from areas where waste is placed for disposal, if applicable.

- Keep access roadways, fire routes and fire department connections clear and accessible for fire department use.

- Maintain the fire protection equipment in good operating condition at all times.

- Participate in fire drills.  Occupants’ participation should be encouraged.

- Have a working knowledge of the building fire and life safety systems.

- If applicable, maintain a list of occupants who have notified supervisory staff that they require assistance during a fire emergency.

- Ensure the building fire and life safety systems are in operating condition.

- Arrange for a substitute in your absence.

- Comply with the Ontario Fire Code.

- In the event of any shutdown of fire and life safety systems, notify Bancroft Fire Department and initiate alternative measures.

Emergency Procedures

Additional Information/Comments

Emergency Procedures

Additional Information/Comments (p.2)

Part 5

Responsibilities of the Owner / Occupant

Please take the time to review this section (1 page).

The building owner/occupant has numerous responsibilities related to fire safety and must ensure that the following measures are enacted:

- Establishment of emergency procedures to be followed at the time of an emergency.

- Appointment and organization of designated supervisory staff to carry out safety   duties.

- Instruction of supervisory staff and other occupants so that they are aware of their responsibilities for fire safety.

- Ensure proper training of all staff for fire emergency procedures, including portable fire extinguisher use, is conducted and reviewed on an annual basis at minimum.

- Holding of fire drills in accordance with the Fire Code, incorporating Emergency    Procedures appropriate to the building.

- Control of fire hazards in the building.

- Maintenance of building facilities and fire separations provided for safety of the occupants.

- Provisions of alternate measures for safety of occupants during shut down of fire    protection equipment.

- Ensuring that checks, tests and inspections as required by the Ontario Fire Code are completed on schedule and that records are retained for a minimum period of two (2) years.

- Post and maintain at least one (1) copy of the fire emergency procedures.

- Keep a copy of the approved Fire Safety Plan on the premises in an approved          location.  Review the Fire Safety Plan with all staff on an annual basis.

- Notification of the Chief Fire Official regarding changes in the Fire Safety Plan.

- Ensure that the information in the Fire Safety Plan is current.

- Ensure a list of occupants requiring assistance during a fire emergency or evacuation is maintained and updated as required.

- Designate and train sufficient alternates to replace supervisory staff during any     absence.

- Division A, Article 1.2.1.1. of the Ontario Fire Code, states ‘Unless otherwise specified, the owner is responsible for carrying out the provisions of this Code.’

Part 6

Fire Hazards

Commercial, Retail and Industrial Properties

A high standard of housekeeping and building maintenance is probably the most important single factor in the prevention of fire.  Listed below are some specific hazards.

- Combustible material stored in non-approved areas.

- Fire and smoke barrier door not operating properly or wedged open.

- Improper storage of flammable liquids and gases.

- Defective electrical wiring and appliances, over-fusing, and the use of extension cords as permanent wiring.

- Clothes dryer lint collector full or improperly vented.

- Careless use of smoking materials.

- Kitchen hoods and filters not cleaned properly/grease laden.

- Improper disposal of oily rags.

In general, occupants should:

- Know how to alarm occupants of building, know where exits are located.

- Call Bancroft Fire Department immediately (9-1-1) whenever you need assistance.

- Know the correct address of the building.

- Notify the building/property management if special assistance is required in the event of an emergency.

- Know the fire alarm signals and the procedures established to implement safe evacuation.

- Know the supervisory staff in your building.

- Report any fire hazard to supervisory staff.

Part 7

Fire Extinguishment, Control or Confinement

Please take the time to review this section (1 page).

In the event a small fire cannot be extinguished with the use of a portable fire            extinguisher or the smoke presents a hazard for the operator, the door to the area should be closed to confine and contain the fire.  Leave the fire area.  Ensure that the Fire Alarm System has been activated and that Bancroft Fire Department has been notified prior to an attempt to extinguish the fire.  Only those persons who are trained and familiar with extinguisher operation may attempt to fight the fire and only if their exit path is unobstructed.  The decision to fight a fire is a voluntary act.

Suggested Operation of Portable Fire Extinguishers

Remember the acronym P.A.S.S.

P - Pull the safety pin

A - Aim the nozzle at the base of the fire

S - Squeeze the trigger handle

S - Sweep from side to side (watch for fire restarting)

Never re-hang extinguishers after use.  Ensure they are properly recharged by a person that is qualified to service portable fire extinguishers and that a replacement extinguisher is provided.

Keep extinguishers in a visible area without obstructions around them.

NOTE:	Prior to using a K-type extinguisher, activate the kitchen extinguishing system to avoid electrocution.

Part 8

Alternative Measures for Occupant Fire Safety

Please take the time to review this section (1 page).

In the event of any shut-down of fire protection equipment systems or part thereof, in excess of 24 hours, the fire department shall be notified in writing.  Occupants will be notified and instructions will be posted as to alternative provisions or actions to be taken in case of emergency.  These provisions and actions must be acceptable to the Chief Fire Official.

All attempts to minimize the impact of malfunctioning equipment will be initiated.  Where portions of a sprinkler or fire alarm system are placed out of service, service to remaining portions must be maintained, and where necessary, the use of watchmen, bull-horns, walkie-talkies, etc. will be employed to notify concerned parties of emergencies.  Assistance and direction for specific situations will be sought from Bancroft Fire Department.

Procedures to be followed in the event of shutdown of any part of a fire protection    system are as follows:

- Notify Bancroft Fire Department, dial (613) 332-2442 (DO NOT USE 911).  Give your name, address and a description of the problem and when you expect it to be corrected.  Bancroft Fire Department is to be notified in writing of shutdowns longer than 24 hours.

- Post notices at all exits and the main entrance, stating the problem and when it is expected to be corrected.

- Have staff or other reliable person(s) patrol the affected area(s) at least once every hour.

- Notify the Bancroft Fire Department and the building occupants when repairs have been completed and systems are operational.

Note:	All shutdowns will be confined to as limited an area and duration as possible.

Cooking operations shall be suspended until the commercial cooking fixed extinguishing system is restored.

Part 9

### Fire Drills

Please take the time to review this section.

Fire drills will be held at least once every 12 months to ensure efficient execution of the Emergency Procedures.  Fire drill records are required to be retained for a period of one year.  Prior to performing a fire drill, ensure the alarm monitoring company has been notified.

FIRE DRILL RECORD

| Date: |  |  | Time: |  |
| --- | --- | --- | --- | --- |

| Manager/Supervisor On-Duty: |  |
| --- | --- |

| Staff Present: |  |
| --- | --- |

| Deficiencies Noted: |  |
| --- | --- |

| General Comments: |  |
| --- | --- |

Part 10

Requirements of the Ontario Fire Code

Please take the time to review this section (1 page).

Check/test/inspect requirements of the Ontario Fire Code:

- To assist you in fulfilling your obligations, included is a list of the portions of the Fire Code that requires checks, inspections and/or tests to be conducted of the facilities.  It is suggested that you read over this list and perform or have performed the       necessary checks, inspections and/or tests for the items that may apply to your property.

- Fire Prevention Officers may check to ensure that the necessary checks, inspections and/or tests are being done, when conducting their inspections.

- This list has been prepared for purposes of convenience only.  For accurate           reference, the Fire Code should be consulted.

Definitions for key words are as follows:

Check		means visual observation to ensure the device or system is in

place and is not obviously damaged or obstructed

Test		means the operation of a device or system to ensure that it will

perform in accordance with its intended operation or function

Inspect	means physical examination to determine that the device or system

will apparently perform in accordance with its intended function

It is stated in the Fire Code that records of all tests and corrective measures are         required to be retained for a period of two years after they are made.

Part 11

Maintenance Requirements of Building

Fire & Life Safety Systems:

General									Responsibility

| Doors in fire separations shall be checked as frequently as necessary to ensure that they remain closed. | Eg: Staff/Contractor |
| --- | --- |
| Exit signs shall be clearly visible and maintained in a clean and legible condition. |  |
| Internally illuminated exit signs shall be kept clearly illuminated at all times, when the building is occupied. |  |

Weekly

| When subject to accumulation of combustible deposits, hoods, filters and ducts shall be checked weekly and be cleaned when such deposits create an undue fire hazard. |  |
| --- | --- |

Monthly

| Doors in fire separations shall be inspected monthly for proper operation. |  |
| --- | --- |

Yearly

| Fire dampers and fire-stop flaps shall be inspected annually, or based on a schedule via contractor acceptable to the Chief Fire Official. |  |
| --- | --- |
| Every chimney, flue and flue pipe shall be inspected annually and cleaned as often as necessary to keep them free from accumulations of combustible deposits. |  |
| Disconnect switches for mechanical air-conditioning and ventilating systems shall be inspected annually to establish that the system can be shut down. |  |
| Spark arresters shall be cleaned annually or more frequently where accumulations of debris will adversely affect operations. Burnt-out arresters shall be repaired or replaced. |  |

### Portable Fire Extinguishers

General									Responsibility

| Each portable extinguisher shall have a tag securely attached to it showing the maintenance or recharge date, the servicing agency and the signature of the person who performed the service. |  |
| --- | --- |
| A permanent record containing the maintenance date, the examiner’s name and a description of any work or hydrostatic testing carried out shall be prepared and maintained for each portable extinguisher. |  |
| All extinguishers shall be recharged after use or as indicated by an inspection or when performing maintenance. When recharging is performed, the recommendations of the manufacturer shall be followed. |  |

Monthly

| Portable extinguishers shall be inspected monthly. |  |
| --- | --- |

Yearly

| Extinguishers shall be subject to maintenance not more than one year apart or when specifically indicated by an inspection. |  |
| --- | --- |
| Maintenance procedures shall include a thorough examination of the three basic elements of an extinguisher: a) mechanical parts b) extinguishing agent c) expelling means |  |

| 5 Years Every five years, pressurized water and carbon dioxide fire extinguishers shall be hydrostatically tested. |  |
| --- | --- |

| 6 Years Every six years, stored pressure extinguishers that require a 12 year hydrostatic test shall be emptied and subjected to the applicable maintenance procedures. |  |
| --- | --- |

Fire Alarm

Responsibility

General

| Fire alarm shall be kept unobstructed. |  |
| --- | --- |
| Fire alarm system power supply disconnect switches shall be locked on in an approved manner. |  |

Daily

| The following daily checks shall be conducted if a fault is established, appropriate corrective action shall be taken. a) Check the principle and remote trouble lights for trouble indication; b) Inspection of the AC power-on light shall be done to ensure its normal operation. |  |
| --- | --- |

Monthly

| Every month the following tests shall be conducted under battery back up power and if a fault is established, appropriate corrective action shall be taken: a) one manual fire alarm initiating device shall be operated, on a rotating basis, and shall initiate an alarm condition b) function of all signal devices shall be ensured c) the annunciator panel shall be checked to ensure correct annunciation d) intended function of the audible and visual trouble signals shall be ensured e) fire alarm batteries shall be checked to ensure that: i) terminals are clean and lubricated where necessary; ii) terminal clamps are clean and tight; iii) electrolyte level and specific gravity, where applicable, meet manufacturer’s specifications |  |
| --- | --- |

Yearly

| Yearly tests conducted by a certified alarm contractor as required by The Ontario Fire Code, Section 1.2.1.2. of Division C, Tests shall be in conformance with CAN/ULC S536, “Inspection and Testing of Fire Alarm Systems”. |  |
| --- | --- |

Sprinkler Systems (Wet)

Responsibility

General

| Auxiliary drains shall be inspected as required to prevent freezing. |  |
| --- | --- |

Weekly

| Except for electrically supervised valves, all valves controlling water supplies to sprinklers and alarm connections shall be checked weekly to ensure that they are sealed or locked in the open position. |  |
| --- | --- |
| Water supply pressure and system air or water pressure shall be checked weekly by using gauges to ensure that the system is maintained at the required operating pressure. |  |

Monthly

| On all sprinkler systems, an alarm test, using the alarm test connection located at the sprinkler valve, shall be performed monthly. |  |
| --- | --- |

Two Months

| All transmitters and water flow devices shall be tested at two month intervals. |  |
| --- | --- |

Six Months

| Gate-valve supervisory switches and other sprinkler system supervisory devices shall be tested at six month intervals. |  |
| --- | --- |

Responsibility

Yearly

| Exposed sprinkler piping hangers shall be checked yearly to ensure that they are kept in good repair. |  |
| --- | --- |
| Sprinkler heads shall be checked at least once per year to ensure that they are kept in good repair. |  |
| Sprinkler heads shall be checked at least once per year to ensure that they are free from damage, corrosion, grease, dust, paint, or whitewash. They shall be replaced where necessary as a result of such conditions. |  |
| On wet sprinkler systems, water-flow alarm test using the most hydraulically remote test connection, shall be performed annually. |  |
| Sprinkler system water pressure shall be tested annually or after any sprinkler system control valve has been operated, with the main drain valve fully open, to ensure that there are no obstructions or deterioration of the main water supply. |  |
| Plugs or caps on Fire Department connections shall be removed annually and the threads inspected of wear, rust or obstruction. Re-secure plugs or caps, wrench tight. If plugs or caps are missing, examine the Fire Department connection for obstructions, back flush if necessary and replace plugs or caps. |  |

Sprinkler Systems (Dry)

Responsibility

General

| Auxiliary drains shall be inspected as required to prevent freezing. |  |
| --- | --- |
| Dry-pipe valve rooms or enclosures in unheated buildings shall be checked as often as necessary when the outside temperature falls below 0o Celsius to ensure that the system does not freeze. |  |

Weekly

| Except for electrically supervised valves, all valves controlling water supplies to sprinklers and alarm connections shall be checked weekly to ensure that they are sealed or locked in the open position. |  |
| --- | --- |
| Water supply pressure and system air or water pressure shall be checked weekly by using gauges to ensure that the system is maintained at the required operating pressure. |  |
| System pressure gauges shall be checked weekly. The system shall be maintained at the required operating pressure. |  |

Monthly

| On all sprinkler systems, an alarm test, using the alarm test connection located at the sprinkler valve, shall be performed monthly. |  |
| --- | --- |

2 Months

| All transmitters and water flow devices shall be tested at two month intervals. |  |
| --- | --- |

Responsibility

3 Months

| The priming water supply for dry pipe systems shall be inspected every three months to ensure that the proper level above the dry pipe valve is maintained. |  |
| --- | --- |

6 Months

| Gate-valve supervisory switches and other sprinkler system supervisory devices shall be tested at six month intervals. |  |
| --- | --- |

Yearly

| Exposed sprinkler piping hangers shall be checked yearly to ensure that they are kept in good repair. |  |
| --- | --- |
| Sprinkler heads shall be checked at least once per year to ensure that they are free from damage, corrosion, grease dust, paint, or whitewash. They shall be replaced where necessary as a result of such conditions. |  |
| Sprinkler system water pressure shall be tested annually or after any sprinkler system control valve has been operated, with the main drain valve fully open, to ensure that there are no obstructions or deterioration of the main water supply. |  |
| Plugs or caps on Fire Department connections shall be removed annually and the threads inspected for wear, rust or obstruction. Re-secure plugs or caps wrench tight. If plugs or caps are missing, examine the Fire Department connection for obstructions, back flush if necessary and replace plugs or caps. |  |
| Dry pipe valves shall be tripped annually by means of the system test pipe, to ensure that they operate satisfactorily and that the sprinkler alarms are in operating condition. A full flow trip test, with the control valve fully open, shall be conducted at least every three years. |  |

15 Years

| Every fifteen years, dry pipe systems shall be inspected for obstructions in the sprinkler piping and if necessary, the entire system shall be flushed of foreign material. |  |
| --- | --- |

Private Fire Hydrants

General									Responsibility

| Hydrants shall be readily available and unobstructed for use at all times. |  |
| --- | --- |

Yearly

| Hydrants shall be inspected annually after each use. |  |
| --- | --- |
| Ensure hydrants are equipped with port caps secured wrench tight. The port caps shall be removed annually and inspected for wear, rust or obstructions. |  |
| The hydrant barrel shall be inspected annually to ensure that no water has accumulated. |  |
| The drain valve shall be inspected for operation if water is found in the hydrant barrel when main valve is closed. |  |
| Hydrant water flow shall be inspected annually and a record shall be kept. |  |

Commercial Cooking Equipment

General									Responsibility

| Commercial cooking equipment exhaust and fire protection systems shall be installed and maintained in conformance with NFPA 96, “Ventilation Control and Fire Protection of Commercial Cooking Operations”. |  |
| --- | --- |
| Ensure wet chemical or alkali based dry chemical portable fire extinguishers are provided to protect commercial cooking equipment and are readily available for use in an emergency. |  |

Weekly

| Hoods, grease removal devices, fans, ducts, and other equipment shall be checked weekly and cleaned at frequent intervals, prior to surfaces becoming heavily contaminated with grease or oily sludge. |  |
| --- | --- |

6 Months

| Inspection and servicing of the fire extinguishing system shall be made at least every six months by properly trained and qualified persons in conformance with NFPA 96. |  |
| --- | --- |

Emergency Lighting System

Responsibility

Daily

| Check pilot lights for indication of proper operation. |  |
| --- | --- |

Monthly

| Batteries shall be inspected monthly and maintained as per manufacturer’s specifications. |  |
| --- | --- |
| Ensure that battery surface is clean and dry. |  |
| Ensure that terminal connections are clean, free of corrosion and lubricated. |  |
| Ensure that the terminal clamps are clean and tight as per manufacturer’s specifications. |  |
| Emergency lighting equipment shall be tested monthly to ensure that the emergency lighting will function upon failure of the primary power supply. |  |

Yearly

| Emergency lighting equipment shall be tested annually to ensure that the units will provide emergency lighting for a duration equal to the design criteria under simulated power failure conditions. |  |
| --- | --- |
| After completion, the charging conditions for voltage and current and the recovery period will be tested annually to ensure that he charging system is in accordance with the manufacturer’s specifications. |  |

Maintenance

Additional Comments

Part 12- Building Schematics

Please take the time to review this page.

LEGEND FOR BUILDING / UNIT FIRE EMERGENCY SYSTEM

|  | Pull Pin For Kitchen Fire Suppression System |
| --- | --- |
|  | Entrance / Exit |
|  | Hydrant |
|  | Siamese Fire Department Connection |
|  | Free Standing Siamese Fire Department Connection |
|  | Valves (General) - Identify The Type Of Valve (Ie. Shut Off For Natural Gas, Sprinklers, Etc.) |
|  | Fire Alarm Control Panel |
|  | Fire Alarm Annunciator |
|  | Fire Safety Plan |
|  | Alarm Monitoring Station |
|  | Emergency Light, Battery-Powered |
|  | Illuminated Exit Sign, Single Face |
|  | Combined Battery-Powered Emergency Light & Illuminated Exit Sign |
|  | Pull Station |
|  | Heat Detector |
|  | Smoke Detector |
|  | Fire Extinguisher - BC Type |
|  | Fire Extinguisher - ABC Type |
|  | Fire Extinguisher - Water |
| H | Hose Cabinet |
|  | Sprinkler Riser, indicate whether Wet or Dry System |
|  | Electrical / Water / Gas (Propane) Main Shut Offs |

Site Plan

(include legend)

Please attach to e-mail, use postal mail (address is on the final page of this document), or fax to (613) 332-2222.  Please indicate your company name so the plan can be attached to your submission.

Floor Plan

(Include Legend)

Please attach to e-mail, use postal mail (address is on the final page of this document), or fax to (613) 332-2222.  Please indicate your company name so the plan can be attached to your submission.

Fire Department Address:

Bancroft Fire Department

33 Chemaushgon Rd.

P.O. Box 790

Bancroft, ON

K0L 1C0

Phone: (613) 332-2442

Email:  FPO@bancroftfire.ca

Website:  www.bancroftfire.ca

Twitter:  @bancroftfire