#### Fire Safety Plan

(Interconnected Smoke Alarms)

Fire Safety Plan – Small Business / Residential Interconnected Smoke Alarm System for:

(Business Name)

(Business Address)

Prepared By                                        Reviewed By

(Person Completing Form)                                            (Fire Inspector)

Signature						        Signature

Date of Approval

Table of Contents

Part #	Topic – Pg #

# Part 1		Introduction:  PG 3

Part 2 (a)	Audit of Building Resources Checklist:  PG 4

Part 2 (b)	Audit of Human Resources:  PG 8

Part 3		Emergency Procedures for Occupants:  PG 9

Part 4		Emergency Procedures for Supervisory Staff:  PG 10

Part 5		Responsibilities of the Owner/Occupant:  PG 14

Part 6	 (a)	Fire Hazards — Residential:  PG 15

Part 6 (b)	Fire Hazards — Commercial:  PG 16

Part 7		Fire Extinguishment, Control or Confinement:  PG 17

Part 8		Alternative Measures for Occupant Fire Safety:  PG 18

Part 9		Fire Drills:  PG 19

Part 10	Requirements of the Ontario Fire Code:  PG 20

Part 11	Maintenance Requirements of Building

Fire & Life Safety Systems:    PG 21

Part 12	Building Schematics, Site Plan/Floor Plan:	PG 40

Part 13	Appendix A – Handout for Residents:  PG 44

Fire Department Contact Info:		PG 46

Part 1

Introduction

The Ontario Fire Code, Section 2.8 requires the implementation of a FIRE SAFETY PLAN for this building/occupancy.  The plan is to be kept in the building in an approved location.

The implementation of the Fire Safety Plan helps to ensure effective utilization of life safety features in a building to protect people from fire.  The required Fire Safety Plan should be designed to suit the resources of each individual building or complex of    buildings.  It is the responsibility of the owner to ensure that the information contained within the Fire Safety Plan is accurate and complete.

The Fire Protection and Prevention Act Part VII, Section 28, states that in the case of an offence for contravention of the fire code, a corporation is liable to a fine of not more than $100,000 and an individual is liable to a fine of not more than $50,000 or imprisonment for a term of not more than one year or both.

This official document is to be kept readily available at all times for use by staff and fire officials in the event of an emergency.

The fire safety plan approved location is      .

SUBMISSION PROCEDURES

At least two (2) copies of the Plan (8 ½ X 11 format) must be submitted to the Chief Fire Official.  Upon approval, one copy will be returned to the author and one copy will be retained by the Fire Department.

The Chief Fire Official is to be notified regarding any subsequent changes in the         approved Fire Safety Plan.

Part 2(a)

Audit of Building Resources Checklist

Occupancy Type

Residential	  Commercial	 Other:

Occupant Load: (if applicable)

Construction Type

Access

Designated Fire Route:		 No     Yes

Nearest Municipal

Hydrant Location:

| Private Hydrants: No Yes (Location(s)): |  |
| --- | --- |
| Lockbox: No Yes (Location(s)): |  |

Heating	 Propane	  Electric		 Other

| Main Gas Shut-off: No Yes (Location(s)): |  |
| --- | --- |

Main Electrical Shut-off Location:

Main Domestic Water Shut-off Location:

###### Smoke Alarm Monitoring Panel (If applicable):

Make:

Model:

Main Panel Location:

Annunciator Panel Location:

Fire Alarm Description:

Sprinkler System:	   No      Yes 		Type:	 Wet    Dry   Other

Connected to the Fire Alarm System:  No      Yes

Location of Sprinkler Room/Shut-off Valves:

Standpipe System:   No      Yes – Refer to Floor Plan

Location of Shut-off/Isolation Valves:

Fire Department

Connection:	No     Yes (Location(s)):

Fire Pump:		 No      Yes (Location(s):

Fire Pump Description:

Fixed Extinguishing System for Commercial Cooking Equipment

No      Yes 		Type:

(i.e. Wet Chemical, Dry Chemical, CO2)

Connected to F/A System:     No      Yes

Ecology Unit:     No      Yes    	Protected by Fixed System:     No      Yes

Fuel Source:	 Natural Gas	 Electric		 Other

Fuel Shut Off for Appliances:	Location:

40BC Extinguisher:	Location:

K Type (wet) Extinguisher (if applicable):	Location:

Other Extinguishing Systems:

No      Yes – If YES, please list “Type” and “Area/Location Protected” in Part 2(a) Additional Information and label “Other Extinguishing Systems.”

Portable Fire Extinguishers (Location(s): Refer to Floor Plan)

No      Yes 		Type(s):

Extra Hazardous Area:  Description/Location: Eg: Confined Crawlspace / Under main building

Is there hazardous materials on site?		 No      Yes

If YES, please list the material and quantity in Part 2(a) Additional Information and label “Hazardous Materials”

Emergency Lighting

No      Yes 			Location(s):

Emergency / Alternative Power

No      Yes – Type:   Battery   Generator   Solar   Other -

Transfer Switch Location:

Generator

Diesel		  Propane           Other

Fuel Supply Location:

Equipment Powered by Generator:

Electromagnetic Locking Devices

No      Yes (manual release switch location):

Alternate Emergency Exits:	 No      Yes - Refer to schematics for location of exits.

Part 2(a)

Additional Information

Please print multiple copies of page if required.

For any additional information not already covered (Hazardous Materials, Back-up Power Systems, etc.):

Part 2(b)

Audit of Human Resources

Business/Building Name:

Address:		      Unit No.

Postal Code:	      Business Phone No.

Business Owner:

Address:

Postal Code:

Phone Number(s):

After Hour Contacts (24 hour telephone numbers)

Manager/Supervisor:       Phone No.

Employee/Title:	      Phone No.

Employee/Title:	      Phone No.

Other:		      Phone No.

Building Owner:

Address:

Postal Code:	       Phone No.

Fire Alarm Monitoring Company:       Phone No.:

Sprinkler Monitoring Company:       Phone No.:

Part 3

Emergency Procedures for Occupants

Please take the time to review this section (1 page).

Emergency procedures signage will be affixed to the wall at all fire alarm pull stations and in elevator lobbies.

IN CASE OF FIRE

Upon Discovery of Fire:

- Leave fire area immediately and close doors.

- Sound Fire Alarm.

- Leave building via nearest Exit.

- Call Fire Department at 9-1-1.

Upon Hearing Fire Alarm:

- Turn off all cooking appliances

- Leave building via nearest Exit

- Close doors behind you

- Do not use elevator

- Wait in a safe location for the Fire Department.

CAUTION

IF YOU ENCOUNTER SMOKE - USE AN ALTERNATE EXIT

DO NOT re-enter the building until you are notified by the Fire Department that it is safe to do so.

Remain Calm

Part 4

Emergency Procedures for Supervisory Staff

Please take the time to review this section (2 pages).

Upon Discovery of Fire

- Leave fire area immediately and close doors.  Alert occupants.

- Sound Fire Alarm and follow the fire alarm supervisory procedures.

- Call 9-1-1 from a safe location.

- Use portable fire extinguisher ONLY IF the fire is small, your exit path is unobstructed and you are trained to do so.

- Exit the building via the nearest exit.

- Await the arrival of the Fire Department at the main entrance.

Upon Hearing of a Fire Condition

- Ensure that the other occupants have been notified of the emergency conditions.

- Notify the Bancroft Fire Department of the emergency condition. Dial 9-1-1 and ask for the Bancroft Fire Department.

- If it is safe to do so, supervise the evacuation of all occupants, including those       requiring assistance.

- Upon the arrival of the firefighters, inform the fire officer of the conditions in the building and co-ordinate the efforts of the Supervisory staff with those of the Fire Department.

- Provide access and vital information to the firefighters as to location of persons, master keys for this occupancy and service rooms, etc.

Related Duties

In general:

- Keep the doors in fire separations closed at all times unless the door is designed to automatically close in the event of a fire emergency.

- Keep access to exits and EXITS, inside and outside, clear of any obstructions at all times.

- Do not permit combustible materials to accumulate in quantities or locations that would constitute a fire hazard.

- Promptly remove all combustible waste from areas where waste is placed for        disposal, if applicable.

- Keep access roadways, fire routes and fire department connections clear and          accessible for fire department use.

- Maintain the fire protection equipment in good operating condition at all times.

- Participate in fire drills.  Occupants’ participation should be encouraged.

- Have a working knowledge of the building fire and life safety systems.

- If applicable, maintain a list of occupants who have notified supervisory staff that they require assistance during a fire emergency.

- Ensure the building fire and life safety systems are in operating condition.

- Arrange for a substitute in your absence.

- Comply with the Ontario Fire Code.

- In the event of any shutdown of fire and life safety systems, notify the Bancroft Fire Department and initiate alternative measures.

Emergency Procedures

Additional Information/Comments

Emergency Procedures

Additional Information/Comments (p.2)

Part 5

Responsibilities of the Owner / Occupant

Please take the time to review this section (1 page).

The building owner/occupant has numerous responsibilities related to fire safety and must ensure that the following measures are enacted:

- Establishment of emergency procedures to be followed at the time of an emergency.

- Appointment and organization of designated supervisory staff to carry out safety   duties.

- Instruction of supervisory staff and other occupants so that they are aware of their responsibilities for fire safety.

- Ensure proper training of all staff for fire emergency procedures, including portable fire extinguisher use, is conducted and reviewed on an annual basis at minimum.

- Holding of fire drills in accordance with the Fire Code, incorporating Emergency    Procedures appropriate to the building.

- Control of fire hazards in the building.

- Maintenance of building facilities and fire separations provided for safety of the occupants.

- Provisions of alternate measures for safety of occupants during shut down of fire    protection equipment.

- Ensuring that checks, tests and inspections as required by the Ontario Fire Code are completed on schedule and that records are retained for a minimum period of two (2) years.

- Post and maintain at least one (1) copy of the fire emergency procedures.

- Keep a copy of the approved Fire Safety Plan on the premises in an approved          location.  Review the Fire Safety Plan with all staff on an annual basis.

- Notification of the Chief Fire Official regarding changes in the Fire Safety Plan.

- Ensure that the information in the Fire Safety Plan is current.

- Ensure a list of occupants requiring assistance during a fire emergency or evacuation is maintained and updated as required.

- Designate and train sufficient alternates to replace supervisory staff during any     absence.

- Division A, Article 1.2.1.1. of the Ontario Fire Code, states ‘Unless otherwise specified, the owner is responsible for carrying out the provisions of this Code.’

Part 6(a)

## Fire Hazards

Please take the time to review this section (2 pages).

Residential Properties

To avoid fire hazards in the building, occupants must:

- Never put burning materials such as cigarettes and ashes into the garbage chute.

- Never dispose of flammable liquids or aerosol cans in these chutes.

- Never force cartons, coat hangers, bundles of paper into the chute because it may become blocked.

- Avoid unsafe cooking practices; deep fat frying, too much heat, unattended stoves, loosely hanging sleeves.

- Avoid careless smoking.  Never smoke in bed.

- Never leave anything that may burn or cause a trip hazard in the halls, corridors and/or stairways.

- Always clean out clothes dryer lint collector before and after use.

- Do not use unsafe electrical appliances, frayed extension cords, overloaded outlets or lamp wire for permanent wiring.

In general, occupants should:

- Know how to alarm occupants of building, know where exits are located.

- Call the Bancroft Fire Department immediately (9-1-1) whenever you need assistance.

- Know the correct address of the building.

- Notify the building owner/property management if special assistance if required in the event of an emergency.

- Know the fire alarm signals and the procedures established to implement safe evacuation.  Read and follow the manufacturers smoke alarm (and CO detector if   applicable) instructions, available from building owner/property management.

- Know the supervisory staff in your building.

- Report any fire hazard to supervisory staff.

- Know the stairwell designation and the crossover floors (if any).

Part 6(b)

Fire Hazards

Commercial, Retail and Industrial Properties

A high standard of housekeeping and building maintenance is probably the most important single factor in the prevention of fire.  Listed below are some specific hazards:

- Combustible material stored in non-approved areas.

- Fire and smoke barrier door not operating properly or wedged open.

- Improper storage of flammable liquids and gases.

- Defective electrical wiring and appliances, over-fusing, and the use of extension cords as permanent wiring.

- Clothes dryer lint collector full or improperly vented.

- Careless use of smoking materials.

- Kitchen hoods and filters not cleaned properly.

- Improper disposal of oily rags.

In general, occupants should:

- Know how to alarm occupants of building, know where exits are located.

- Call the Bancroft Fire Department immediately (9-1-1) whenever you need assistance.

- Know the correct address of the building.

- Notify the building/property management if special assistance is required in the event of an emergency.

- Know the fire alarm signals and the procedures established to implement safe evacuation.

- Know the supervisory staff in your building.

- Report any fire hazard to supervisory staff.

- Know stairwell designation and the crossover floors (if any).

###### Commercial

Part 7

Fire Extinguishment, Control or Confinement

Please take the time to review this section (1 page).

In the event a small fire cannot be extinguished with the use of a portable fire            extinguisher or the smoke presents a hazard for the operator, the door to the area should be closed to confine and contain the fire.  Leave the fire area.  Ensure that the Fire Alarm System has been activated and that the Bancroft Fire Department has been notified prior to an attempt to extinguish the fire.  Only those persons who are trained and familiar with extinguisher operation may attempt to fight the fire and only if their exit path is unobstructed.  The decision to fight a fire is a voluntary act.

Suggested Operation of Portable Fire Extinguishers

Remember the acronym P.A.S.S.

P - Pull the safety pin

A - Aim the nozzle at the base of the fire

S - Squeeze the trigger handle

S - Sweep from side to side (watch for fire restarting)

Never re-hang extinguishers after use.  Ensure they are properly recharged by a person that is qualified to service portable fire extinguishers and that a replacement extinguisher is provided.

Keep extinguishers in a visible area without obstructions around them.

NOTE:	Prior to using a K-type extinguisher, activate the kitchen extinguishing system to avoid electrocution.

Part 8

Alternative Measures for Occupant Fire Safety

Please take the time to review this section (1 page).

In the event of any shut-down of fire protection equipment systems or part thereof, in excess of 24 hours, the fire department shall be notified in writing.  Occupants will be notified and instructions will be posted as to alternative provisions or actions to be taken in case of emergency.  These provisions and actions must be acceptable to the Chief Fire Official.

All attempts to minimize the impact of malfunctioning equipment will be initiated.  Where portions of a sprinkler or fire alarm system are placed out of service, service to remaining portions must be maintained, and where necessary, the use of watchmen, bull-horns, walkie talkies, etc. will be employed to notify concerned parties of emergencies.  Assistance and direction for specific situations will be sought from the Bancroft Fire Department.

Procedures to be followed in the event of shutdown of any part of a fire protection    system are as follows:

- Notify the Bancroft Fire Department, dial (613) 332-2442 (DO NOT USE 911).  Give your name, address and a description of the problem and when you expect it to be corrected.  The Bancroft Fire Department is to be notified in writing of shutdowns longer than 24 hours.

- Post notices on all floors by elevators and in the lobby entrance, stating the problem and when it is expected to be corrected.

- Have staff or other reliable person(s) patrol the affected area(s) at least once every hour.

- Notify the Bancroft Fire Department and the building occupants when repairs have been completed and systems are operational.

Note:  All shutdowns will be confined to as limited an area and duration as possible.

Cooking operations shall be suspended until the commercial cooking fixed extinguishing system is restored.

Part 9

### Fire Drills

Fire drills will be held at least once every       months to ensure efficient execution of the Fire Safety Plan.  Fire drill records are required to be retained for a period of one year.  Prior to performing a fire drill, ensure the alarm monitoring company has been notified.

FIRE DRILL RECORD

Date: _______________________________ 		Time: ____________________________

Manager/Supervisor On-Duty:	_________________________________________________

Staff Present:			_________________________________________________

_________________________________________________

Deficiencies Noted:		_________________________________________________

_________________________________________________

_________________________________________________

_________________________________________________

_________________________________________________

General Comments:		_________________________________________________

_________________________________________________

_________________________________________________

_________________________________________________

_________________________________________________

Part 10

Requirements of the Ontario Fire Code

Please take the time to review this section (1 page).

Check/test/inspect requirements of the Ontario Fire Code:

- To assist you in fulfilling your obligations, included is a list of the portions of the Fire Code that requires checks, inspections and/or tests to be conducted of the facilities.  It is suggested that you read over this list and perform or have performed the       necessary checks, inspections and/or tests for the items that may apply to your property.

- Fire Prevention Officers may check to ensure that the necessary checks, inspections and/or tests are being done, when conducting their inspections.

- This list has been prepared for purposes of convenience only.  For accurate           reference, the Fire Code should be consulted.

Definitions for key words are as follows:

Check		means visual observation to ensure the device or system is in

place and is not obviously damaged or obstructed

Test		means the operation of a device or system to ensure that it will

perform in accordance with its intended operation or function

Inspect	means physical examination to determine that the device or system

will apparently perform in accordance with its intended function

It is stated in the Fire Code that records of all tests and corrective measures are         required to be retained for a period of two years after they are made.

Part 11

Maintenance Requirements of Building

Fire & Life Safety Systems:

General									Responsibility

| Doors in fire separations shall be checked as frequently as necessary to ensure that they remain closed. | Eg: Staff/Contractor |
| --- | --- |
| Exit signs shall be clearly visible and maintained in a clean and legible condition. |  |
| Internally illuminated exit signs shall be kept clearly illuminated at all times, when the building is occupied. |  |

Weekly

| When subject to accumulation of combustible deposits, hoods, filters and ducts shall be checked weekly and be cleaned when such deposits create an undue fire hazard. |  |
| --- | --- |

Monthly

| Doors in fire separations shall be inspected monthly for proper operation. |  |
| --- | --- |

Yearly

| Fire dampers and fire-stop flaps shall be inspected annually, or based on a schedule via contractor acceptable to the Chief Fire Official. |  |
| --- | --- |
| Every chimney, flue and flue pipe shall be inspected annually and cleaned as often as necessary to keep them free from accumulations of combustible deposits. |  |
| Disconnect switches for mechanical air-conditioning and ventilating systems shall be inspected annually to establish that the system can be shut down. |  |
| Spark arresters shall be cleaned annually or more frequently where accumulations of debris will adversely affect operations. Burnt-out arresters shall be repaired or replaced. |  |

Portable Fire Extinguishers

General									Responsibility

| Each portable extinguisher shall have a tag securely attached to it showing the maintenance or recharge date, the servicing agency and the signature of the person who performed the service. |  |
| --- | --- |
| A permanent record containing the maintenance date, the examiner’s name and a description of any work or hydrostatic testing carried out shall be prepared and maintained for each portable extinguisher. |  |
| All extinguishers shall be recharged after use or as indicated by an inspection or when performing maintenance. When recharging is performed, the recommendations of the manufacturer shall be followed. |  |

Monthly

| Portable extinguishers shall be inspected monthly. |  |
| --- | --- |

Yearly

| Extinguishers shall be subject to maintenance not more than one year apart or when specifically indicated by an inspection. |  |  |  |
| --- | --- | --- | --- |
| Maintenance procedures shall include a thorough examination of the three basic elements of an extinguisher: a) mechanical parts b) extinguishing agent c) expelling means |  |  |  |
| Every twelve months, pump tank water, and pump tank calcium chloride base antifreeze types of extinguishers shall be recharged with new chemicals or water, as applicable |  |  |  |
| 5 Years Every five years, pressurized water and carbon dioxide fire extinguishers shall be hydrostatically tested. |  |  |  |
| 6 Years Every six years, stored pressure extinguishers that require a 12 year hydrostatic test shall be emptied and subjected to the applicable maintenance procedures. |  |  |  |

Fire Alarm/Voice Communications Systems

General									Responsibility

| Fire alarm and voice communication system components shall be kept unobstructed. |  |
| --- | --- |
| Fire alarm system power supply disconnect switches shall be locked on in an approved manner. |  |

Daily

| The following daily checks shall be conducted if a fault is established, appropriate corrective action shall be taken. a) Check the principle and remote trouble lights for trouble indication. b) Inspection of the AC power-on light shall be done to ensure its normal operation. |  |
| --- | --- |

Monthly

| Every month the following tests shall be conducted and if a fault is established, appropriate corrective action shall be taken: a) one manual fire alarm initiating device shall be operated, on a rotating basis, and shall initiate an alarm condition b) function of all signal devices shall be ensured c) the annunciator panel shall be checked to ensure correct annunciation d) intended function of the audible and visual trouble signals shall be ensured e) fire alarm batteries shall be checked to ensure that: i) terminals are clean and lubricated where necessary; ii) terminal clamps are clean and tight; iii) electrolyte level and specific gravity, where applicable, meet manufacturer’s specifications |  |
| --- | --- |

| Voice paging capability to one zone shall be tested monthly on a rotational basis. |  |
| --- | --- |

Monthly (continued)							Responsibility

| One emergency telephone shall be tested monthly on a rotational basis for operation and correct indication at control unit. |  |
| --- | --- |
| Loudspeakers shall be tested monthly as an all-call signal to ensure they function as intended. |  |
| At least one firefighter’s emergency telephone shall be tested monthly on a rotational basis to ensure communication with the control unit. All telephones shall be tested each year. |  |

Yearly

| Yearly tests conducted by a certified alarm contractor as required by The Ontario Fire Code, Section 1.1.5.3. Tests shall be in conformance with CAN/ULC S536, “Inspection and Testing of Fire Alarm Systems”. |  |
| --- | --- |
| Voice communications between floor areas and the central alarm control facility shall be tested annually, as required for fire alarm initiating and signalling devices. |  |

Smoke Alarms

General									Responsibility

| Ensure dwelling unit smoke alarms are maintained in operating condition. |  |  |
| --- | --- | --- |
| Ensure a copy of the smoke alarm manufacturer’s Maintenance instructions or approved alternative has been provided. |  |  |
| Ensure dwelling unit smoke alarms are tested annually at minimum. |  |  |

Standpipe Systems

Monthly									Responsibility

| Hose cabinets shall be inspected monthly to ensure that the hose and equipment are in the proper position and appear to be operable. |  |
| --- | --- |

Yearly

| Plugs or caps on Fire Department connections shall be removed annually and the threads inspected for wear, rust or obstruction. Re-secure plugs or caps, wrench tight. |  |  |
| --- | --- | --- |
| If plugs or caps are missing, examine the Fire Department connections for obstructions, back flush if necessary, and replace plugs or caps. |  |  |
| Hose valves shall be inspected annually to ensure that they are tight and that there is no water leakage into the hose. |  |  |
| Standpipe hose shall be removed and re-racked annually and after use. Any worn gaskets in the couplings, at the hose valve and at the nozzle shall be replaced. |  |  |

Sprinkler Systems (Wet)

General									Responsibility

| Auxiliary drains shall be inspected as required to prevent freezing. |  |
| --- | --- |

Weekly

| Except for electrically supervised valves, all valves controlling water supplies to sprinklers and alarm connections shall be checked weekly to ensure that they are sealed or locked in the open position. |  |  |
| --- | --- | --- |
| Water supply pressure and system air or water pressure shall be checked weekly by using gauges to ensure that the system is maintained at the required operating pressure. |  |  |

Monthly

| On all sprinkler systems, an alarm test, using the alarm test connection located at the sprinkler valve, shall be performed monthly. |  |
| --- | --- |

Two Months

| All transmitters and water flow devices shall be tested at two-month intervals. |  |
| --- | --- |

Six Months

| Gate-valve supervisory switches and other sprinkler system supervisory devices shall be tested at six month intervals. |  |
| --- | --- |

Yearly									Responsibility

| Exposed sprinkler piping hangers shall be checked yearly to ensure that they are kept in good repair. |  |  |
| --- | --- | --- |
| Sprinkler heads shall be checked at least once per year to ensure that they are kept in good repair. |  |  |
| Sprinkler heads shall be checked at least once per year to ensure that they are free from damage, corrosion, grease, dust, paint, or whitewash. They shall be replaced where necessary as a result of such conditions. |  |  |
| On wet sprinkler systems, water-flow alarm test using the most hydraulically remote test connection, shall be performed annually. |  |  |
| Sprinkler system water pressure shall be tested annually or after any sprinkler system control valve has been operated, with the main drain valve fully open, to ensure that there are no obstructions or deterioration of the main water supply. |  |  |
| Plugs or caps on Fire Department connections shall be removed annually and the threads inspected of wear, rust or obstruction. Re-secure plugs or caps, wrench tight. If plugs or caps are missing, examine the Fire Department connection for obstructions, back flush if necessary and replace plugs or caps. |  |  |

Sprinkler Systems (Dry)

General									Responsibility

| Auxiliary drains shall be inspected as required to prevent freezing. |  |
| --- | --- |
| Dry-pipe valve rooms or enclosures in unheated buildings shall be checked as often as necessary when the outside temperature falls below 0o Celsius to ensure that the system does not freeze. |  |

Weekly

| Except for electrically supervised valves, all valves controlling water supplies to sprinklers and alarm connections shall be checked weekly to ensure that they are sealed or locked in the open position. |  |
| --- | --- |
| Water supply pressure and system air or water pressure shall be checked weekly by using gauges to ensure that the system is maintained at the required operating pressure. |  |
| System pressure gauges shall be checked weekly. The system shall be maintained at the required operating pressure. |  |

Monthly

| On all sprinkler systems, an alarm test, using the alarm test connection located at the sprinkler valve, shall be performed monthly. |  |
| --- | --- |

2 Months

| All transmitters and water flow devices shall be tested at two month intervals. |  |
| --- | --- |

3 Months									Responsibility

| The priming water supply for dry pipe systems shall be inspected every three months to ensure that the proper level above the dry pipe valve is maintained. |  |
| --- | --- |

6 Months

| Gate-valve supervisory switches and other sprinkler system supervisory devices shall be tested at six month intervals. |  |
| --- | --- |

Yearly

| Exposed sprinkler piping hangers shall be checked yearly to ensure that they are kept in good repair. |  |
| --- | --- |
| Sprinkler heads shall be checked at least once per year to ensure that they are free from damage, corrosion, grease dust, paint, or whitewash. They shall be replaced where necessary as a result of such conditions. |  |
| Sprinkler system water pressure shall be tested annually or after any sprinkler system control valve has been operated, with the main drain valve fully open, to ensure that there are no obstructions or deterioration of the main water supply. |  |
| Plugs or caps on Fire Department connections shall be removed annually and the threads inspected for wear, rust or obstruction. Re-secure plugs or caps wrench tight. If plugs or caps are missing, examine the Fire Department connection for obstructions, back flush if necessary and replace plugs or caps. |  |
| Dry pipe valves shall be tripped annually by means of the system test pipe, to ensure that they operate satisfactorily and that the sprinkler alarms are in operating condition. A full flow trip test, with the control valve fully open, shall be conducted at least every three years. |  |

15 Years

| Every fifteen years, dry pipe systems shall be inspected for obstructions in the sprinkler piping and if necessary, the entire system shall be flushed of foreign material. |  |
| --- | --- |

Water Supplies for Firefighting (Fire Pumps)

Daily										Responsibility

| The temperature of pump rooms shall be checked daily during freezing weather. |  |
| --- | --- |

Weekly

| Valves controlling water supplies exclusively for fire protection systems shall be inspected weekly to ensure that they are fully open and sealed or locked in that position. |  |
| --- | --- |
| Fire pumps shall be started once per week at rated speed. The fire pump discharge pressure, suction pressure, lubricating oil level, operative condition of relief valves, priming water level and general operating conditions shall be inspected. |  |
| Internal combustion engine fire pumps shall be operated once per week for a sufficient time to bring the engine up to normal operating temperature. The storage batteries, lubrication systems and fuel supplies shall be inspected. |  |

Yearly

| Fire pumps shall be tested annually at full rated capacity to ensure that they are capable of delivering the rated flow. |  |
| --- | --- |

Water Supplies for Firefighting (Hydrants)

General									Responsibility

| Hydrants shall be readily available and unobstructed for use at all times. |  |
| --- | --- |

Yearly

| Hydrants shall be inspected annually after each use. |  |
| --- | --- |
| Ensure hydrants are equipped with port caps secured wrench tight. The port caps shall be removed annually and inspected for wear, rust or obstructions. |  |
| The hydrant barrel shall be inspected annually to ensure that no water has accumulated. |  |
| The drain valve shall be inspected for operation if water is found in the hydrant barrel when main valve is closed. |  |
| Hydrant water flow shall be inspected annually and a record shall be kept. |  |

Water Supplies for Firefighting (Water Tanks)

Daily										Responsibility

| Water tank heat equipment, tank enclosure and/or water temperature shall be checked daily during freezing weather. |  |
| --- | --- |

Weekly

| Water levels and air pressure in pressure tanks shall be checked weekly and the relief valves on the air and the water lines shall be inspected weekly. |  |
| --- | --- |

Monthly

| Water level in gravity tanks shall be inspected monthly. |  |
| --- | --- |

Yearly

| An annual inspection shall be made of water tanks for fire protection, tank supporting structures and water supply systems including piping, control valves, check valves, heating systems, mercury gauges and expansion joints to ensure that they are in operating condition. |  |
| --- | --- |
| Cathodic protection equipment in water tanks shall be inspected annually. |  |

2 Years

| Water tanks shall be checked every two years for corrosion. |  |
| --- | --- |

5 Years

| Water tanks shall be inspected every five years and scraped and repainted as required. |  |
| --- | --- |

Smoke Shafts and Venting Equipment

General									Responsibility

| Access to windows and panels required for venting floor areas and vents to vestibules permitted to be manually openable shall be kept free of obstructions, openable without keys and operable at times. |  |
| --- | --- |

6 Months

| All elevators in an elevator shaft that is intended for use as a smoke shaft be inspected semi-annually to ensure that on activation of the fire alarm system, the elevators will return to the street floor and remain inoperative. |  |
| --- | --- |

Yearly

| A closure in an opening to the outdoors at the top of a smoke shaft, shall be inspected annually to ensure that it will open: a) manually, outside from the building b) on a signal from the smoke/heat actuated device in the smoke shaft, and; c) when a closure in an opening between a floor area and the smoke shaft opens |  |
| --- | --- |
| Controls for air-handling systems for venting in the event of a fire, shall be inspected annually to ensure that air is exhausted from each floor area to the outdoors. |  |

5 Years

| Closures in vent openings into smoke shafts from each floor shall be inspected sequentially over a period not to exceed 5 years. |  |
| --- | --- |

Smoke Control Measures

General									Responsibility

| Where smoke control measures contained in the supplement to the National Building Code of Canada 1995, Chapter 3, “Measures for Fire Safety in High Buildings” are used, the inspections and tests shall be as outlined in Section 7.3 of the National Fire Code of Canada. |  |
| --- | --- |
| Where a smoke control system is designed to meet the requirements of The Ontario Building Code, the inspections and tests shall be in accordance with procedures established by the designer of the system. |  |

Commercial Cooking Equipment

General									Responsibility

| Commercial cooking equipment exhaust and fire protection systems shall be installed and maintained in conformance with NFPA 96, “Ventilation Control and Fire Protection of Commercial Cooking Operations”. |  |
| --- | --- |
| Ensure wet chemical or alkali based dry chemical portable fire extinguishers are provided to protect commercial cooking equipment and are readily available for use in an emergency. |  |

Weekly

| Hoods, grease removal devices, fans, ducts, and other equipment shall be checked weekly and cleaned at frequent intervals, prior to surfaces becoming heavily contaminated with grease or oily sludge. |  |
| --- | --- |

6 Months

| Inspection and servicing of the fire extinguishing system shall be made at least every six months by properly trained and qualified persons in conformance with Ontario Fire Code, Section 6.8.1.1. |  |
| --- | --- |

Emergency Lighting System

Daily										Responsibility

| Check pilot lights for indication of proper operation. |  |
| --- | --- |

Monthly

| Batteries shall be inspected monthly and maintained as per manufacturer’s specifications. |  |
| --- | --- |
| Ensure that battery surface is clean and dry. |  |
| Ensure that terminal connections are clean, free of corrosion and lubricated. |  |
| Ensure that the terminal clamps are clean and tight as per manufacturer’s specifications. |  |
| Emergency lighting equipment shall be tested monthly to ensure that the emergency lighting will function upon failure of the primary power supply. |  |

Yearly

| Emergency lighting equipment shall be tested annually to ensure that the units will provide emergency lighting for a duration equal to the design criteria under simulated power failure conditions. |  |
| --- | --- |
| After completion, the charging conditions for voltage and current and the recovery period will be tested annually to ensure that he charging system is in accordance with the manufacturer’s specifications. |  |

Emergency Power Systems

General									Responsibility

| Emergency power systems shall be inspected, tested and maintained in conformance with CSA C282, “Emergency Electrical Power Supply for Buildings”. |  |
| --- | --- |
| To ensure continued reliable operation, the emergency power supply equipment shall be operated and maintained in accordance with manufacturer’s instructions. |  |
| At least two copies of the instruction manual shall be maintained. |  |

Monthly

| The emergency electrical power shall be completely tested monthly as follows: a) Simulate a failure of the normal power supply. b) Arrange so that: i) an engine generator set operates under at least 30% of the rated load for 60 minutes and; ii) all automatic transfer switches are operated under load. c) Include an inspection for correct function of all auxiliary equipment such as radiator shutter control, coolant pumps, fuel transfer pumps, oil coolers and engine room ventilation controls. d) Record all instrument readings associated with the prime mover and generator and verification that they are normal. e) Log and report as further prescribed in the manual of instruction for operation and maintenance. - Check fuel supply for sufficient quantity. |  |
| --- | --- |

Annually

| Test the generator, control panel, and transfer switch in conformance with CSA C282, “Emergency Electrical Power Supply for Buildings”. |  |
| --- | --- |

Maintenance

Additional Comments

Part 12- Building Schematics

Please take the time to review this page.

LEGEND FOR BUILDING / UNIT FIRE EMERGENCY SYSTEM

|  | Pull Pin For Kitchen Fire Suppression System |
| --- | --- |
|  | Entrance / Exit |
|  | Hydrant |
|  | Siamese Fire Department Connection |
|  | Free Standing Siamese Fire Department Connection |
|  | Valves (General) - Identify The Type Of Valve (Ie. Shut Off For Natural Gas, Sprinklers, Etc.) |
|  | Fire Alarm Control Panel |
|  | Fire Alarm Annunciator |
|  | Fire Safety Plan |
|  | Alarm Monitoring Station |
|  | Emergency Light, Battery-Powered |
|  | Illuminated Exit Sign, Single Face |
|  | Combined Battery-Powered Emergency Light & Illuminated Exit Sign |
|  | Pull Station |
|  | Heat Detector |
|  | Smoke Detector |
|  | Fire Extinguisher - BC Type |
|  | Fire Extinguisher - ABC Type |
|  | Fire Extinguisher - Water |
| H | Hose Cabinet |
|  | Sprinkler Riser, indicate whether Wet or Dry System |
|  | Electrical / Water / Gas (Propane) Main Shut Offs |

Site Plan

(Include Legend)

Please attach to e-mail, use postal mail (address is on the final page of this document), or fax to (613) 332-2222.  Please indicate your company name so the plan can be attached to your submission.

Floor Plan

(Include Legend)

Please attach to e-mail, use postal mail (address is on the final page of this document), or fax to (613) 332-2222.  Please indicate your company name so the plan can be attached to your submission.

Part 13

Appendix A

**These pages are to be given to rental unit occupants and reviewed with new tenants to ensure they are aware of the buildings fire safety planning**

Emergency Procedures for Occupants Upon discovery of fire: - Leave fire area immediately and close doors - Sound fire alarm - Leave building via nearest exit - Call Bancroft Fire Department at 911 - If available, brief superintendent of the problem Upon hearing the fire alarm: - Turn off all cooking appliances - Leave building via nearest exit - Close doors behind you - Wait in a safe location for the Fire Department CAUTION: IF YOU ENCOUNTER SMOKE –USE ALTERNATIVE EXIT ROUTE DO NOT re-enter the building until you are notified by the Fire Department that it is safe to do so. Smoke Alarm Maintenance Information for Tenants The Ontario Fire Code requires that every place of residence have smoke alarms installed and kept in working condition on every level of the residence. Smoke alarms are very important for your and your neighbours safety by giving early warning of smoke or fire. Your landlord is responsible for installing smoke alarms and keeping them in working condition, including testing, repairs and replacement as necessary. Your landlord must also act to correct any problem or concern you report about the operation of your smoke alarm. Your residence has been provided with a smoke alarm that is □ battery operated or □ hard wired. For your protection, you are encouraged to take part in ensuring that the smoke alarms are operational and to co-operate with the landlord in carrying out the necessary testing and maintenance..

**These pages are to be given to rental unit occupants and reviewed with new tenants to ensure they are aware of the buildings fire safety planning**

Here are some steps that you can take:. Notify the landlord when the low battery signal is activated and make arrangements for replacement of the battery.. Notify the landlord if the smoke alarm is damaged and make arrangements for the repair or replacement of the unit.. When you have been absent for seven or more days (such as vacation), arrange for the smoke alarms to be tested by the landlord to ensure that the smoke alarms are operable (on battery operated smoke alarms only).. Contact your local fire department if you have serious concerns about the operability of your smoke alarm or any other fire safety matters in your building... The Fire Code specifies that "no person shall intentionally disable a smoke alarm so as to make it inoperable". A tenant or any other person who intentionally disables a smoke alarm is guilty of a provincial offence and may be subject to a fine.. For your safety and the safety of other residents, tenants should: - Avoid unsafe cooking practices, deep fat frying, unattended stoves, loosely hanging sleeves - If there is a smoker in residence, engage in safe practices. Do not leave unattended. - Use candles safely. Do not leave unattended at any time. - Do not use unsafe electrical appliances, frayed extension cords, overloaded outlets or lamp wiring as permanent wiring – check for the CSA rating on electrical appliances - Know the fire alarm signal and how to safely evacuate the building - Report any fire hazard to supervisory staff - Notify the superintendent of any special assistance that you may require to evacuate the building

Fire Department Address:

Bancroft Fire Department

33 Chemaushgon Rd.

P.O. Box 790

Bancroft, ON

K0L 1C0

Phone: (613) 332-2442

Email:  FPO@bancroftfire.ca

Website:  www.bancroftfire.ca

Twitter:  @bancroftfire